NUCLEAR TECHNOLOGY

# How Reactors Work

## Conversion of Uranium to Plutonium

63 neutrons

URANIUM-238

5 fissions

58 absorbed

URANIUM-239

(half-life = 23.5 min)

NEPTUNIUM-239

(half-life = 2.3 days)

PLUTONIUM-239

(half-life = 24,000 years)

Beta emission

Beta emission

Neutrons have very large energy:

- Need to be slowed down by “moderation”

- Releases energy  neutron hits particle and “shares” its energy with it

## Neutron Histories in Fast Reactors

Neutron Events - LMFBR

FISSIONS

100

NEUTRONS PRODUCED

292

Pu239 ABSORPTIONS

116

U235 ABSORPTIONS

3

U238 ABSORPTIONS

134

U235

FISSIONS

3

U238

FISSIONS

13

Pu239

FISSIONS

3

FISSIONS

100

## Breeding Processes

292 NEUTRONS

LOSSES

39

U235

FISSIONS

3

116 neutrons

134 neutrons

PLUTONIUM-239

URANIUM-238

FISSIONS

84

ABSORPTION

32

ABSORPTION

121

FISSIONS

13

PLUTONIUM-239

121 atoms of Pu-239 produced

116 atoms of Pu-239 consumed		  Net gain of 5 atoms of Pu-239  “BREEDING”

## Distribution of Energy from U-235 Fission

| Process | Energy (1012) J |
| --- | --- |
| Fission Products | 64 |
| Fission Neutrons | 2 |
| Prompt  radiation | 3 |
| Fission product decay (heat) |  |
|  radiation | 3 |
|  radiation | 3 |
| Neutrinos | 5 |
| TOTAL | 80 |

Main problem	 CANNOT switch entire plant off

 Must continue to cool reactor for ever

## Magnox Reactor

### Problems:

- Magnesium interacts with cooling water

- Steam generator separate from reactor  safer to contain all in one

## Advanced Gas Cooled Reactor (AGR)

### Operation:

- 40 bar pressure

- CO2 cooled

- Integral boilers

- Concrete pressure vessels

- Enriched fuel

- Safety bonus  self-contained reactor, all within concrete block

### AGR Fuel Elements:

Problems:

- Optimisation of heat transfer

- Moderator attack

  - Graphite interacts with CO2 to produce CO

  - CO2+C2CO

- Methane addition reverses reaction  carbon deposition

  - Carbon coating insulates the can slightly

  - Build-up of deposit reduces turbulence

- Hence operating range for AGR exists

## Pressurised Water Reactor (PWR)

### Operation:

- Cooling:

  - Via single-phase water at 150 bar

  - Steam generated at typically 70 bar

  - Water  v. high heat transfer coefficient (GOOD)

- Enriched fuel

- World’s most prevalent reactor

- Steel pressure vessel contains reactor  safe

- Pressuriser  generates steam to push water down

### PWR Fuel Elements:

- Stainless steel cladding

- Fuel pressurised

- Uranium oxide pellets

- Water is also the moderator

## Boiling Water Reactor

### Operation:

- Water boils inside the core at 70 bar

- 10% w/w of fluid leaving the top of the column is steam

### Advantages:

- Coolant used directly to generate steam

### Problems:

- Water reacts with uranium to make tritium  slightly radioactive steam circuit

- Not completely isolated system

## CANDU (Canadium Deuterium/Uranium Reactor)

### Operation:

- Coolant:

  - Heavy water

  - No need to enrich it

### CANDU Fuel Elements:

- Natural uranium  no enrichment

- D2O investment high

- Pressure tube reactor  problem with pressure tubes

## Boiling Water Graphite Moderated Direct Cycle Reactor (RBMK )

### Operation:

- Moderator  graphite

- Coolant  water

- No high pressure vessel

- USSR reactor

### Problem:

- Unstable

## Sodium Cooled Fast Reactor

### Operation:

- Coolant  sodium

- No moderator

- Work with pure plutonium

- Core is small (i.e. size of a dustbin)

- Need to get heat out of reactor v. quickly  liquid metal used

### Problems:

- Integrity of steam generator

- Water/sodium interaction possible when leaks present

## Conclusion

- Wide variety of reactors

- Increasing tendency to standardise on PWR

- Problems:

  - Stead-state design (coolant technology)

  - Transient effects (safety)

  - Fuel processing

  - Fission product disposal

# Reactor Cooling Systems

## General Requirements for Coolant

Ideal coolant would have:

- High specific heat capacity (Cp)

- High heat transfer coefficient

- Good nuclear properties

  - Low neutron absorption

  - No radioactive isotopes formed

  - Appropriate moderation properties

- Low cost and easy availability

- Compatibility with reactor circuit

- Easily pumped – low viscosity

NO COOLANT FULFILS ALL THESE REQUIREMENTS

## Figure of Merit

Figure of Merit defined for lowest pumping power P for given L, A, M, Q and temperature rise T.

Pressure drop (p) across channel given by:

Δp=1ρMA22fLD

Where		f = friction factor = MDAη−0.2

|  | fluid density | kg/m3 |
| --- | --- | --- |
|  | fluid viscosity | N.s/m3 |
| A | cross sectional area | m2 |
| M | mass flowrate | kg/s |

Pumping power, P:

P=Δp×V=Δpmρ

	P=1ρ2M3A22fLD			(1)

Where

| V | volumetric flowrate | m3/s |
| --- | --- | --- |
| p | pressure drop | Pa |

Heat transfer Q given by:

Q=MCpΔT

Hence equation (1) can be substituted for M:

P=1ρ2A2Q3Cp3ΔT32fLD

Same method can be used on friction factor equation:

f=MDAη−0.2=QDCpΔTη−0.2

Thus P is proportional to:

P∝2LA2D1.2Q2.8ΔT2.8η0.2Cp2.8ρ2

For fixed L, A, D, Q, T  P is minimum when:

η0.2Cp2.8ρ2 is MINIMUM or when

Figure of Merit (F)=Cp2.8ρ2η0.2 is a MAXIMUM

## Water as Reactor Coolant

Light water has:

- High availability and low cost

- High Figure of Merit

Problems are:

- Low boiling point

  - High pressure required to achieve moderate efficiencies

- Neutron absorption relatively high

  - Enriched uranium required

- Corrosive at high temperature

  - Special containment materials required

  - Strict control of water chemistry

## Maximum Fuel Temperature

| Element | Temperature (C) | Notes |
| --- | --- | --- |
| Uranium metal | 650 | Crystal structure change gives swelling at higher temperatures |
| Uranium oxide | 2800 | Melting point of oxide |

## Maximum Pellet Temperature

Define total energy per metre of fuel as R (W/m2). Rate of energy release within radius r:

a

r

r2a2R=q×2π⋅r

Where

| r | Inner radius | m |
| --- | --- | --- |
| a | Outer radius | m |

Thermal conduction equation:

q=R2πrr2a2=−λdTdr−λdT=R2πa2rdr

Where

|  | Thermal conductivity of fuel | (W/m2)/(K/m) |
| --- | --- | --- |

Temperature at radius r, Tr, is:

Tr=T0+R4πλ1−r2a2

Where

| T0 | Temperature on outside of pellet | K |
| --- | --- | --- |

Centre (maximum) temperature:

Tmax=T0+R4πλ

## Maximum Clad Temperature

| Clad type | Temperature (C) | Notes |
| --- | --- | --- |
| Magnesium alloy (Magnox) | 450 |  |
| AGR stainless steel | 750 | Melting point = 1400C |
| PWR zircalloy | 320 | Reacts rapidly with water at T>500C producing H2. Exothermic reaction with T>1000C |
| BWR zircalloy | 300 |  |
| Sodium cooled fast reactor | 750 |  |

## Typical Heat Transfer Coefficients

| Compound | Heat transfer coeff. (W/m2.K) |
| --- | --- |
| Water | 30,000 |
| Boiling water | 60,000 |
| High pressure CO2 | 1,000 |
| Liquid sodium | 55,000 |

Need for augmentation for gas-cooled systems:

- Increase surface area by finning (Magnox fuel elements)

  - Fins increase area relative to smooth surface

  - Promote mixing of gas

  - Augmentation by factor of 5-6

- Roughness elements on surface (AGR fuel pin)

  - Increase of surface area is small

  - Roughness elements break up boundary layer  increase  by 2.5 times

  - Also increase pressure drop

## Coolants - Gaseous

### Air:

- Used in Windscale natural uranium filter

- Oxidant for graphite

### Carbon Dioxide:

- Complex chemistry

- Corrosion of graphite  carbon deposition

### Helium:

- Inert gas

- Coolant in High Temperature Gas Cooled Reactor (HTGCR or HTR)

### Steam:

- Better heat transfer than CO2

- Superheaters attempted

- Not used significantly

### Nitrogen Oxides:

- N2O4/NO2

- Proposed in USSR

## Coolants – Liquid

### Light Water:

- Can be used as coolant and moderator

- Needs dome enrichment of uranium

### Heavy Water:

- Less neutron absorption than light water

- Can be used without enrichment  CANDU

### Organic Fluids:

- Polyphenyls – high temperature (300C) and low pressure (10 bar)

- Degradation

### Molten Salts:

- Often proposed – not much used!

- Homogeneous reactors

### Liquid Metals:

- Sodium and potassium

- Sodium cheaper and safer

## Coolants – Boiling

### Light Water (BWR):

- Radiolysis problem

  - H2O  H2 and O2  steam phase

  - Recombination much slower than for water phase

  - O2  stress corrosion cracking (major problem with BWR’s)

### Liquid Metals:

- Boiling potassium

- Proposed for space reactors

## Alternative Coolant Circuits

### Loop Type:

- Core in vessel

- Primary coolant circulator and steam generator outside

### Integral Type:

- Core, primary coolant circulator and steam generator in single vessel

- Feed water in, steam out

### Pool Type:

- Core and primary coolant circulator immersed in pool pf coolant

- E.g. “swimming pool reactor”  fast breeder

## Conclusion

- Very wide variety of coolants proposed

- Only limited range have actually been used

- Pressurised light water emerged as most popular

- Sodium cooling highly efficient for fast reactors

# Two-Phase Flow and Heat Transfer

## Two-phase flow patterns – Vertical Tubes

PICTURE

## The Homogeneous Model

### Assumptions:

- Treats fluid as single fluid (c.f. single phase flow)

- Equal velocities for two phases

Homogeneous density:

ρH=mv=mAmAxρG+mA1−xρL=ρLρGxρL+1−xρG

Where

| H | Homogeneous density | kg/m3 |
| --- | --- | --- |
| m | Mass flux | kg/s |
| v | Volumetric flowrate | m3/s |
| x | Quality (fraction of mass flow flowing as vapour) | - |
| G | Void fraction of vapour | - |

Void fraction:

εG=vGv=xx+1−xρGρL

## Separated Flow Model

### Assumptions:

- Two fluids in separate regions

- Each with a given velocity

- uG≠uL

Define slip ratio as:

S=uGuL=1

Hence for this flow model  S≠1

Mean fluid density in element:

ρT=ρL1−εG+ρGεG

Hence, void fraction /slip ratio relationship becomes:

εG=xx+S1−xρGρL

## Homogeneous Continuity (mass) Equation

For CHANNEL ELEMENT:

0=UρHA+δz∂∂zUρHAOUT−UρHAunderbracealignlIN+Aδz∂ρH∂tACCUMULATION

Where

| H | Homogeneous density | kg/m3 |
| --- | --- | --- |
| U | Total volume flux | m3/s |
| t | Time | s |

Rearranging gives:

∂∂zUρHA+A∂ρH∂t=0

## Homogeneous Momentum Equation

Momentum equation takes into account the following:

Sum of forces on element = Sum of forces due to pressure, gravity and wall shear

Hence momentum decreases/increases depending on forces

mUA+δz∂∂zmUAIN−mUAunderbracealignlOUT+∂∂tmAδzACCUMULATION=pA−pA+δzA∂p∂zPRESSURE−gρHAδzsinαunderbracealignlGRAVITY−τ0PδzunderbracealignlWALL SHEAR

Rearranging the equation by dividing throughout (Az):

	∂m∂t+1A∂m2A/ρH∂z=−∂p∂z−gρHsinα−τ0PA

Where

| p | Fluid pressure (assumed constant over cross-section) | Pa |
| --- | --- | --- |
| g | Acceleration due to gravity | m/s2 |
|  | Angle of alignment | radians |
| 0 | Wall shear stress | N/m2 |
| P | Channel periphery | - |

## Homogeneous Energy Equation

0=UAρHe+δz∂∂zUAρHeOUT−UAρHe+qP+qvAδzunderbracealignlIN+Aδz∂∂tρHμ+u2ρH2ACCUMULATION

Rearranging gives:

ρH∂e∂t+U∂e∂z=qPA+qv+∂p∂t

Where

| e | Energy convected per unit mass of fluid |  |
| --- | --- | --- |
| h | Enthalpy | kJ/kg |
|  | Internal energy of fluid |  |
| q | Wall heat flux | kW |
| qv | Volumetric heat generation rate |  |

## Conservation Equations – Balance Element

Separated flow model  six equation model

- Two flow regions: liquid and vapour

- Liquid: continuity, momentum and energy balance	(3 eqns.)

- Vapour: continuity, momentum and energy balance	(3 eqns.)

- Equations may be summed to give overall balance

## Continuity Equation for Liquid Phase

### Mass Out:

ρL1−εGuLA+δz∂∂zρL1−εGuLA+meδz

### Mass In:

−ρL1−εGuLA

### Accumulation:

+∂∂tρL1−εGAδz

Where

| G | Void fraction of vapour | - |
| --- | --- | --- |
| u | Liquid phase velocity | m/s |
| A | Cross-sectional area | m2 |
| me | Rate of conversion of liquid to vapour per unit length | kg/s |

Simplifying all three terms, we obtain:

∂∂tρL1−εGA+∂∂zρLuL1−εGA=−me			(2)

## Continuity Equation for Vapour Phase

Similarly to liquid phase:

∂∂tρGεGA+∂∂zρGuGεGA=me						(3)

## Combined Continuity Equation

Adding (2) and (3) and noting that:

m=ρLuL1−εG+ρGεGuG

ρT=εGρG+1−εGρL

We obtain:

∂∂tρTA+∂∂zmA=0

## Momentum Equation for Liquid

−1−εG∂p∂z−ρLg1−εGsinα−τ0PA+τiPiA=∂∂tρLuL1−εG+1A∂∂zρLAuL21−εG

Steady-state, constant area duct:

−1−εG∂p∂z−ρLg1−εGsinα−τ0PA+τiPiA=∂∂zρLuL21−εG

## Momentum Equation for Vapour

−εG∂p∂z−ρGgεGsinα−τiPiA=∂∂tρGuGεG+1A∂∂zρGεGAuG2

Steady-state, constant area duct:

−εG∂p∂z−ρGgεGsinα−τiPiA=∂∂zρGεGuG2

## Combined Momentum Equation

−∂p∂z−ρTgsinα−τ0PA=∂∂tρLuL1−εG+ρGuGεG+1A∂∂zρLAuL21−εG+ρGAuG2εG

## Post-Dryout Heat Transfer – Nil Evaporation Case

- Droplets do not evaporate in post-dryout region

- All heat goes into heating  low m, low p

Length

Temperature

DRYOUT

xEQ = 100%

WALL

BULK VAPOUR

xEQ

xDO

TSAT

## Post-Dryout Heat Transfer – Equilibrium Case

- Droplets evaporate at rate sufficient to maintain vapour at TSAT

- Vapour velocity increases and Tw decreases along the channel

BULK VAPOUR

Length

Temperature

DRYOUT

xEQ = 100%

WALL

xEQ

xDO

TSAT

## Conclusion

- Two-phase flow and heat transfer of crucial importance in reactor heat transfer

- Pre-dryout heat transfer not important in core but governing in steam generator in some cases

- Post-dryout heat transfer vital in governing maximum clad temperature

# Critical Heat Flux

## Critical Heat Flux – Definition

CHF synonyms: “Dryout”, “Burnout”, Boiling Crisis”, “DNB”, “Boiling Transition”

### Definitions:

- For heat flux controlled system, CHF corresponds to INORDINATE INCREASE in surface temperature following small change in system parameter (e.g. heat flux, mass flux, inlet subcooling)

- For surface temperature controlled system, CHF corresponds to condition where there is an INORDINATE DECREASE in surface heat flux following change in system parameter

## Parametric Effects on CHF – Fixed length and diameter

hsub

m

qcrit

m

qcrit

Tsub=0

High p

Low p

p

qcrit

Tsub=0

m fixed

pcrit

Tsub = Tsat - Tin

hsub = Cp,L  Tsub

## Parametric Effects on CHF – Fixed mass flux and hsub=0

L

Pcrit

Note: Horizontal channels have lower CHF due to segregation

L

qcrit

d

qcrit

d = tube diameter

Pcrit= power input to achieve CHF

## Critical Heat Flux Mechanisms – Subcooled and low quality

PICTURE

## Critical Heat Flux Mechanisms – Annular flow

PICTURE

- Film dryout by evaporation and entrainment  dominant mechanism

## CHF Predictions in Annular Flow – Parameters

E

D

mLF

mLE

d

z

mLF=mLEπd2/4

dmLFdz=4DD−E−qhLG

Where

| D | Deposition rate per unit area of tube surface |
| --- | --- |
| E | Entrainment rate per unit area of tube surface |

Equilibrium Flow:

D=E

Non-equilibrium Flow:

D≠E

 Correlation for both required

Usual form:

D=kC

Where

| k | Deposition mass transfer coefficient | m/s |
| --- | --- | --- |
| C | Homogeneous concentration of drops in core | kg/m3 |

# LOCA (Loss of Coolant Accident) Phenomena

## Operational States

### Normal Operation:

Operation at full power

### Operational Transients:

Startup and shutdown

On-line refuelling (AGR)

### Upset Conditions:

Unexpected faults. E.g. turbine trips, loss of offsite power

### Emergency Conditions:

Break in small pipe

Relief valve stuck open

### Limiting Fault Conditions (Design Basis Accidents):

Design to cope with by engineered safety systems. E.g. large pipe break

## Fuel Element Behaviour with Increasing Temperature

| Temperature (C) | Phenomenon |
| --- | --- |
| 350 | Approximate cladding temperature during power operation. |
| 800-1500 | Cladding is perforated or swells as a result of rod internal gas pressure in the post-accident environment; some fission gases released; solid reactions between stainless steels and Zircaloy begin; clad swelling may block some flow channels. |
| 1450-1500 | Zircaloy steam reaction may produce energy in excess of decay heat; gas absorption embrittles Zircaloy, hydrogen formed. Steel alloy melts. |
| 1550-1650 | Zircaloy steam reaction may be autocatalytic unless Zircaloy is quenched by immersion. |
| 1900 | Zircaloy melts, fission product released from UO2 becomes increasingly significant above 1877 C. |
| 2700 | UO2 and ZrO2 melt. |

## Small Break LOCAs – Pipe sizes

### Big Pipe Break:

- Pressure lowered immediately

- Allows water to enter vessel  refill

- NO PROBLEM

### Small Pipe Break:

- Pressure remains high

- No water allowed into vessel  refill impossible

- VERY SERIOUS

## Small Break LOCAs – Energy outflows

LOCA governed by the size of break and by substance that leaves the vessel

- Mass lost as steam – GOOD

  - Low mass flowrate

  - High enthalpy change

- Mass lost as waster – BAD

  - High mass flowrate

  - Low enthalpy change

## AGR reactor – Pressurised CO2 circuit

- CO2 circulated by blowers

- Operating pressure = 40 bar

- Boilers inside pressure vessel

## AGR Reactor – Operating states

### Normal Operation:

Operation at full power

### Operational Transients:

Startup and shutdown (operator)

On-line refuelling

### Upset Conditions:

Loss of offsite power

Turbine trips

Secondary side faults

### Emergency Conditions:

Loss of site power (countered by diesel generators)

### Limiting Fault Conditions (Design Basis Accidents):

Depressurisation following break of circuit

Control rod withdrawal

Single channel blockage

DBA = depressurisation

## AGR – Depressurisation fault

- Reactor trips and remains at full pressure  OK

  - Natural convection enough to circulate CO2

- Reactor trips and depressurises but on-site diesel power maintained  OK

  - Diesel power provides low pressure

  - Low pressure coolant flow sufficient to remove decay heat

- Reactor trips, depressurisation and failure of all power  PROBLEM

  - Fuel melts

## Conclusion

- Heat generation and removal is key issue

- Design over full range of operational states is vital

- What seems to be the extreme case is sometimes not

- Important to analyse and learn as much as possible from actual accidents

# Exmples of LOCAs

### Three Mile Island

### Chernobyl

# Computer Codes

## Classification of Computer Codes

- Nuclear safety codes and derivatives:

  - TRAC (QUAC, PLAC)

  - RELAP (ATHENA)

  - RETRAN

  - CATHARE

- Generic CFD codes:

  - FLOW3D

  - PHOENICS

  - FLUENT

- Specialist codes:

  - Annular flow:	HANA

  - Reflood:		QFLOOD

## Conclusions

- Great care to ensure that equations are appropriate and correctly coded

- Numerical aspects need careful attention, particularly order of differencing scheme and nodalisation

- Main problem area is that of closure relationships. An oversimplifies phenomenological approach can be worse than a purely empirical one

- Standard Numerical Benchmark and Physical Benchmark (Data Set) tests have a vital role in obtaining Quality Assured codes